APGA Summary of Control Room Management Rule

Who is a “controller subject to this rule?

The following definitions are included in the rule:

§ 192.3 Definitions

Control room means an operations center staffed by personnel charged with the responsibility for remotely monitoring and controlling a pipeline facility.

Controller means a qualified individual who remotely monitors and controls the safety-related operations of a pipeline facility via a SCADA system from a control room, and who has operational authority and accountability for the remote operational functions of the pipeline facility.

Supervisory Control and Data Acquisition (SCADA) system means a computer-based system or systems used by a controller in a control room that collects and displays information about a pipeline facility and may have the ability to send commands back to the pipeline facility.

To determine if the rule applies to any of your employees answer the following questions:

- Do you have a control room as defined above? If no, you have no controllers subject to this rule.

- If the answer to #1 is yes, do any of the personnel remotely monitor and control the safety-related operations of a pipeline facility via a SCADA system as SCADA is defined above? If no, you have no controllers subject to this rule. The key phrases are underlined.

  - A person that monitors and controls via a SCADA system, but is not monitoring safety-related operations is not a controller.

  - A person who monitors and controls safety-related operations, but not via a SCADA system is not a controller. Note, however, that PHMSA asserts that someone who monitors via SCADA but controls via SCADA or any other means is a controller.

If the answers to both #1 and #2 are yes, you have controllers subject to this rule. You must:

- Update your O&M Manual to include the applicable control room management procedures [described below].

- Update you Emergency plans to include actions required to be taken by a controller during an emergency in accordance with §192.631.

- Develop and follow written control room management procedures that include the following requirements:

  - Fatigue mitigation. Each operator must implement the following methods to reduce the risk associated with controller:

    - Establish shift lengths and schedule rotations that provide controllers off-duty time sufficient to achieve eight hours of continuous sleep;

    - Educate controllers and supervisors in fatigue mitigation strategies and how off-duty activities contribute to fatigue;

    - Train controllers and supervisors to recognize the effects of fatigue; and

    - Establish a maximum limit on controller hours-of-service, which may provide for an emergency deviation from the maximum limit if necessary for the safe operation of a pipeline facility.

  - Compliance validation. Upon request, operators must submit their procedures to the appropriate State agency.

  - Compliance and deviations. An operator must maintain for review during inspection:

    - Records that demonstrate that the 4 items under controller fatigue have been complied with (education and training records for controllers and supervisors; and

    - Documentation to demonstrate that any deviation from the procedures required by this section was necessary for the safe operation of a pipeline facility.

The APGA Security and Integrity Foundation (SIF) has developed a model CRM procedures and training for employees and supervisors that addresses the above requirements.

If your system is an distribution system with more than 250,000 meters or operates transmission pipe that includes compressors, then the written CRM procedures must include all of the above, plus the following:

- Roles and responsibilities. Each operator must define the roles and responsibilities of a controller during normal, abnormal, and emergency operating conditions. To provide for a controller's prompt and appropriate response to operating conditions, an operator must define each of the following:

  - A controller's authority and responsibility to make decisions and take actions during normal operations;

  - A controller's role when an abnormal operating condition is detected, even if the controller is not the first to detect the condition, including the controller's  responsibility to take specific actions and to communicate with others;

  - A controller's role during an emergency, even if the controller is not the first to detect the emergency, including the controller's responsibility to take specific actions and to communicate with others; and

  - A method of recording controller shift-changes and any hand-over of responsibility between controllers.

- Provide adequate information. Each operator must provide its controllers with the information, tools, processes and procedures necessary for the controllers to carry out the roles and responsibilities the operator has defined by performing each of the following:

  - Implement sections 1, 4, 8, 9, 11.1, and 11.3 of API RP 1165  whenever a SCADA system is added, expanded or replaced, unless the operator demonstrates that certain provisions are not practical for the SCADA system used;

  - Conduct a point-to-point verification between SCADA displays and related field equipment when field equipment is added or moved and when other changes that affect pipeline safety are made to field equipment or SCADA displays;

  - Test and verify an internal communication plan to provide adequate means for manual operation of the pipeline safely, at least once each calendar year, but at intervals not to exceed months;

  - Test any backup SCADA systems at least once each calendar year, but at intervals not to exceed 15 months; and

  - Establish and implement procedures for when a different controller assumes responsibility, including the content of information to be exchanged.

- Alarm management. Each operator using a SCADA system must have a written alarm management plan to provide for effective controller response to alarms. An operator’s plan must include provisions to:

  - Review SCADA safety-related alarm operations using a process that ensures alarms are accurate and support safe pipeline operations;

  - Identify at least once each calendar month points affecting safety that have been taken off scan in the SCADA host, have had alarms inhibited, generated false alarms, or that have had forced or manual values for periods of time exceeding that required for associated maintenance or operating activities;

  - Verify the correct safety-related alarm set-point values and alarm descriptions at least once each calendar year, but at intervals not to exceed 15 months;

  - Review the alarm management plan required by this paragraph at least once each calendar year, but at intervals not exceeding 15 months, to determine the effectiveness of the plan;

  - Monitor the content and volume of general activity being directed to and required of each controller at least once each calendar year, but at intervals not to exceed 15 months, that will assure controllers have sufficient time to analyze and react to incoming alarms; and

  - Address deficiencies identified during the above activities

- Change management. Each operator must assure that changes that could affect control room operations are coordinated with the control room personnel by performing each of the following:

  - Establish communications between control room representatives, operator’s management, and associated field personnel when planning and implementing physical changes to pipeline equipment or configuration;

  - Require its field personnel to contact the control room when emergency conditions exist and when making field changes that affect control room operations; and

  - Seek control room or control room management participation in planning prior to implementation of significant pipeline hydraulic or configuration changes.

- Operating experience. Each operator must assure that lessons learned from its operating experience are incorporated, as appropriate, into its control room management procedures by performing each of the following:

  - Review incidents to determine if control room actions contributed to the event and, if so, correct, where necessary, deficiencies related to:

    - Controller fatigue;

    - Field equipment;

    - The operation of any relief device;

    - Procedures;

    - SCADA system configuration; and

    - SCADA system performance.

  - Include lessons learned from the operator’s experience in the training program required by this section.

- Training. Each operator must establish a controller training program and review the training program content to identify potential improvements at least once each calendar year, but at intervals not to exceed 15 months. An operator’s program must provide for training each controller to carry out the roles and responsibilities defined by the operator. In addition, the training program must include the following elements:

  - Responding to abnormal operating conditions likely to occur simultaneously or in sequence;

  - Use of a computerized simulator or non-computerized (tabletop) method for training controllers to recognize abnormal operating conditions;

  - Training controllers on their responsibilities for communication under the operator’s emergency response procedures;

  - Training that will provide a controller a working knowledge of the pipeline system, especially during the development of abnormal operating conditions; and

  - For pipeline operating setups that are periodically, but infrequently used, providing an opportunity for controllers to review relevant procedures in advance of their application.